## Slide 1: Automatic Nozzles
Notes: The Automatic Nozzle concept is relatively new to the fire service.
Constant pressure, variable flow more accurately describes the automatic nozzle.
This section will explain the operation, benefits, advantages and disadvantages.
Automatic nozzle performance will be compared with single and selectable nozzle performance.

## Slide 2: Hand Held Stream Evolution...
1960’s & 70’s
Automatic pressure regulating nozzles invented
Notes: Single flow and selectable flow nozzles were widely used throughout the 1950’s and 1960’s.
During a typical fire attack, water supplies can fluctuate dramatically, causing single and selectable flow nozzle performance to suffer greatly.
Chief C. H. McMillan, of the Gary, Indiana Fire Task Force, realized the need for effective fire streams in large flow operations, where water supplies are continuously changing and stretched to their limits, and where fire streams need to be most effective.
On a paper napkin, he drew the first drawing of his idea, to automatically regulate the nozzle pressure, and therefore create the most effective stream possible with the available flow.
As water supplies fluctuate, the automatic nozzle compensates for this by adjusting itself to the flow available maintaining optimum nozzle pressure.

## Slide 3: Pressure Regulation Concept
Notes: The force of the water pushing against the baffle, compresses the spring, and allows the baffle to open.
The primary baffle, attached to the pressure control unit, varies the discharge opening of the nozzle, depending on the flow being delivered to the nozzle.
This maintains a constant, proper nozzle pressure over a wide flow range.
This allows the flow being supplied to be delivered at the proper nozzle pressure and correct velocity.

## Slide 4: How Does Pressure Regulation Work?
Notes: As more water pressure is placed against the baffle, the spring compresses more, and the baffle opens farther to deliver the additional flow, while maintaining a constant nozzle pressure.
The concept is very similar to that of a pressure relief valve on a pumper. If set at 100 psi, the relief valve will open when pressure goes above 100 psi, allowing excess flow through the relief valve. If increased pressure needs to be relieved, the valve opens farther, relieving more flow, and maintaining the 100 psi setting.
One important difference is that the automatic nozzle will open at pressures below 100 psi, allowinging some flow of water before it reaches 100 psi.

## Slide 5: Pressure Stays Constant as Flow Changes
Notes: The nozzle pressure will stay constant as the flow is increased, because of the spring regulating the nozzle pressure.
Note that the baffle moves out farther and the opening becomes bigger, allowing more water to be delivered.

## Slide 6: Baffle Opens as Flow Increases
Notes: The baffle regulates the amount of water (flow) leaving the nozzle.
Final shaping of the stream is done by the stream shaper.
This automatic adjustment of the opening is like having an infinite number of gallonage selections.

## Slide 7: Nozzle Pressure Automatic & Fixed Flow Nozzles
Notes: This chart shows the relationship of single gallonage nozzles’ and an automatic nozzle’s flow and pressure characteristics.
The single gallonage nozzles have basically one pressure that will deliver one flow with an effective stream velocity.
The automatic maintains that basic nozzle pressure, only over a wide range of flows.
This allows an effective stream velocity over a wide range of flows, automatically.
As pump pressures and flows supplying the nozzles fluctuates, the automatic nozzle adjusts itself to compensate and give an effective stream velocity, while a manually adjusted nozzle requires constant calculations and adjustments by the pump and nozzle operators.

## Slide 8: Automatic Master Stream Nozzle
Notes: The automatic pressure regulation feature allows one nozzle to have the flows of many nozzles or flow selections.
The flow changes are done automatically, instead of manually.

## Slide 9: Automatic Nozzle Benefits...
Consistent hard-hitting streams
Correct nozzle pressure with available flow
Maximum reach with available water
Able to adjust to varying water supply conditions
Nozzle reaction is a direct indication of flow
Nozzle flow control (with slide valve)
Notes: Correct nozzle pressure and stream velocity provide consistent, hard-hitting streams.
Available flow is delivered with correct nozzle pressure.
This allows maximum stream reach with available water.
As water supply fluctuates, nozzle automatically adjusts for best stream.
Nozzle reaction is a direct indication of flow, as nozzle pressure is constant.
If nozzle is provided with a slide-type valve instead of a ball valve, nozzleman flow control is also achieved.

## Slide 10: Disadvantages of Automatic Nozzles...
Higher initial cost
Design unfamiliar to repair personnel
May not provide adequate water at extremely low pressures
Stream may look good, but may not be providing adequate water for extinguishment or protection
The need for a Standard Operating Guideline for minimum pump pressures
Notes: Typically automatic nozzles cost slightly more because of more parts and more critical design and manufacturing processes.
Repair personnel may not be familiar with the design and operation of the automatic nozzle.
If adequate pressure is not provided, nozzle will have very minimal flow.
Stream may “look good” but may not be providing enough water for extinguishment or protection.
Standard operating guidelines are needed to provide a minimum pump discharge pressure to assure adequate flow and firefighter protection.

## Slide 11: Comparison of Reaction @ 150 GPM
75 psi 67.5 lb/f
100 psi 79.2 lb/f
125 psi 88.5 lb/f
150 psi 97.2 lb/f
Nozzle Pressure
Nozzle Reaction
Notes: As shown in the section on single and selectable gallonage nozzles, the nozzle reaction is a function of flow and nozzle pressure.
With a constant flow, nozzle reaction force increases with increase in nozzle pressure.

## Slide 12: Nozzle Pressure, Reaction, & Flow Automatic Nozzles
Notes: With single gallonage nozzles, reaction force may increase due to increased nozzle pressure, not increased flow.
With automatic nozzles, since nozzle pressure is constant, an increase in nozzle reaction indicate a directly relational increase in flow.